[image: image1.jpg]



TECHNICAL DATA SHEET NO: FIRE

VERSION: 3 -1/7/14
PAGE: 3 of 3

PRINT DATE: 7/2/2014
[image: image2.jpg]






	Colour
	Product Code
	Pack Size
	Box Qty

	White
	FIRE
	C3
	25

	Brown
	FIREMATEBN
	C3
	25

	Grey
	FIREMATEGY
	C3
	25


Product Description
EVERFLEX FIRE MATE is a five hour rated, one part, emulsion acrylic based, intumescent Acoustic sealant that gives a firm yet flexible seal to joints in a variety of fire rated structures. Tested following the principles of BS EN 1366-4:2006 as detailed in Warrington Fire Research Report No. 181967 (May 2009).  Acoustic rated to BS EN ISO 140/3. Tested for air permeability to EN13141-1. The product, in suitably designed joints will resist the passage of fire for up to 5 hours. The selected fillers used in this formulation also make it suitable for use as an acoustic sealant.
Benefits
· When exposed to heat, it swells greater than 3 x its original   size, so creating a char that will resist  the passage of  fire for up to 5  hours.

· No priming required for most construction substrates

· Permanently flexible with more than 100% elongation to ISO8339 
· For use in joints up to 50mm wide.

· Excellent acoustic properties for sound deadening - Average noise reduction of 35.9db (100-3150Hz)

· Non slump - easy to apply and tool off.

· Fast cure - tack free in 15 minutes.

· Overpaintable.
· Certified under the harmonized European standard EN15651 for façade for interior applications in compliance with the Construction Product Regulation
Areas For Use
· Sealing joints, voids and irregular holes in fire walls, partitions and other structures; also for maintaining  the integrity  of pipes and cables that penetrate them.

· For internal perimeter pointing of fire rated door and window frames.

Limitations
· Not for use on substrates that may bleed oils, solvents or plasticisers.

· Not for use where joints are constantly immersed in water, or as part of structural glazing systems.

Surface Preparation
All surfaces must be clean, dry and dust free.  All loose or flaking surface coatings, and old sealant and mastic joints, should be removed before application.

Application 

The surfaces to be must be clean, dry and free from dust, grease and other contaminants.

Improve adhesion by wiping surface with EVERBUILD GLASS CLEANER allowing all solvent to evaporate before applying sealant. Priming is generally not required, although we always advise testing small areas prior to use. Large voids should first be filled with EVERBUILD FIREFOAM B1 to  maximize fire rating.
Cut the tip of the cartridge taking care not to damage the thread. Apply nozzle and cut at an angle of 45o with an opening slightly larger than the gap to be sealed. Apply using a standard sealant gun. Best results will be obtained by keeping an even pressure on the trigger and keeping the gun at a constant angle to the surface being sealed. To ensure a proper bond, always smooth the sealant down with a spatula or piece of wood wetted with linseed oil or white spirits. An improved joint appearance can be achieved by placing masking tape to both sides of the joint, removing within 5 minutes of application

Single seal joints should be on the fire rated side of the structure.
Specific Data

	Slump:
	Nil in joints up to 50mm and 0mm to ISO7390

	Max Joint Width:

	50mm

	Working tome:
	10 minutes

	Skin over time:

	10 minutes

	Tack free time:
	15 minutes

	Joint movement:

	+ - 5% of original size

	Cure rate:

	3mm/24hrs at 50%  Relative Humidity +23°C

	Fire test temp:
	1160°C - intumescent @ ca. 135°C

	Cleaning:
	Uncured with a dampened cloth

	Packaging:
	C3 plastic cartridges


FIRE RATING TABLE

FIRE TEST RESULTS – WALL SPECIMENS

	SPECEMIN
	GAP FACE MATERIAL COMBINATION
	WIDTH/DEPTH MM
	BACKING MATERIAL
	INTEGRITY (MINS)
	INSULATION

(MINS)

	E
	Aerated concrete/steel
	30/15
	PE open cell foam
	300
	91

	F
	Aerated concrete/aerated concrete
	20/10
	PE open cell foam
	300
	300

	G
	Aerated concrete/aerated concrete
	10/10
	PE open cell foam
	300
	#

	H
	Aerated concrete/aerated concrete
	30/15
	PE open cell foam
	300
	215


FLOOR SPECIMENS

	SPECEMIN
	GAP FACE MATERIAL COMBINATION
	WIDTH/DEPTH MM
	BACKING MATERIAL
	INTEGRITY (MINS)
	INSULATION

(MINS)

	A
	Aerated concrete/aerated concrete
	30/15
	PE open cell foam
	300
	66

	B
	Aerated concrete/aerated concrete
	20/10
	PE open cell foam
	300
	133

	C
	Aerated concrete/aerated concrete
	10/10
	PE open cell foam
	300
	#

	D
	Aerated concrete/aerated concrete
	50/25
	PE open cell foam
	300
	214


# Evaluation against the insulation criteria of the standard could not occur due to the width of the specimen.

The overall test was discontinued after a period of 300 mins.
Health & Safety
Consult MSDS for full list of hazards

Storage

Store in cool dry conditions between + 5’C and 30’C.  PROTECT FROM FROST

Shelf Life

24 months from date of manufacture
The technical data contained herein is based on our present knowledge and experience and we cannot be held liable for any errors, inaccuracies, omissions or editorial failings that result from technological changes or research between the date of issue of this document and the date the product is acquired. Before using the product, the user should carry out any necessary tests in order to ensure that the product is suitable for the intended application. Moreover, all users should contact the seller or the manufacturer of the product for additional technical information concerning its use if they think that the information in their possession needs to be clarified in any way, whether for normal use or a specific application of our product. Our guarantee applies within the context of the statutory regulations and provisions in force, current professional standards and in accordance with the stipulations set out in our general sales conditions. The information detailed in the present technical data sheet is given by way of indication and is not exhaustive. The same applies to any information provided verbally by telephone to any prospective or existing customer.
EVERFLEX FIRE MATE SEALANT








PAGE  

